## Slide 1
VICTRIX PRO V2

## Slide 2
VICTRIX PRO V2 range
Condensing wall-hung boiler (central heating only)
VICTRIX PRO V2 35
VICTRIX PRO V2 55
VICTRIX PRO V2 80
VICTRIX PRO V2 68
VICTRIX PRO V2 100
VICTRIX PRO V2 120
VICTRIX PRO V2 150
VICTRIX PRO V2 180

## Slide 3
With the renewal of the VICTRIX PRO range, we are improving performance and system arrangements, as well as expanding the range of light commercial condensing wall-hung boilers, with the aim of achieving an upgrade of our offer in the Professional segment.
These aspects are the basis of the intervention that has been implemented; the main targets have been:
extension of the heat output range up to 180 kW, with consequent expansion of the number of models;
electronics update to achieve greater system arrangements;
reduction of overall dimensions in cascade installations;
possibility of functioning with mixtures up to 20 vol.% of hydrogen.
Premise

## Slide 4
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 5
Main features
Central heating boiler (possibility to connect an external storage tank with 3-way valve kit for DHW production)
Available output : 35, 55, 60, 68, 80, 100, 120, 150 ,180 kw;
Modulation range from 10% to 100% (up to model 120);
Pneumatic gas valve, as on the current range (different codes for Natural Gas and LPG) ;
Modulating low consumption circulators;
Setting and programming with buttons and wide display;
Can manage 2 heating zones; ( 1 High temp. and 1 Low temp. by mixing valve)
IPX5D electrical insulation;
Outdoor installation with cover kit;
Frost protection until -5°C CH and DHW ( with optional until -15°C);
“Simple cascade” installation (max 5 boilers without cascade regulator);
Stainless steel condensing module (much appreciated characteristic in this market segment);

## Slide 6
Main features
Standard C type configuration, without upper cover (optional) concentric and twin flue pipes available; With this optional kits the B23 type configuration is possible: with air inlet B23 terminal for indoor installation, or with upper cover (for outdoor installation);
“Simple cascade” (without cascade regulator), with an increase in the number of generators that can be connected, up to 15;
For indoor installation, inside the cabinet (up to 150 model) and outdoor in open areas (with optional cover kit), IPX5D protection index;
Through the new boiler electronics it is possible to manage 2 system CH Zones + 1 DHW circuit;
Available communication protocols: Modbus for BMS systems, OpenTherm (two OT inputs available for commercial thermoregulation, one for each zone), EBV BUS;
Maximum working pressure of 4,4 bar (for models up to 80 kW), 6 bar for higher heat output models (different safety valve);

## Slide 7
VICTRIX PRO 55-60-68-80 V2
Dimensions and connections
Key:
V - Electrical supply
G - Gas supply
R - System return
M - System delivery
SC - Condensate drain (Ø13mm min. internal)
Models | Height (mm) | Width (mm) | Depth (mm)
 | 851 (986) | 440 | 499
 |  |  | 627
Connections |  |  | 
FLUE | GAS | SYSTEM | 
 | G | R | M
D. 110 | ¾” | 1’’ 1/2 | 1’’ 1/2

## Slide 8
VICTRIX PRO 100-120-150 V2
Dimensions and connections
Models | Height (mm) | Width (mm) | Depth (mm)
100-120 | 1098 | 600 | 557
150 | 1233 |  | 627
Connections |  |  | 
FLUE | GAS | SYSTEM | 
 | G | R | M
D. 110 | 1’’ | 1’’ 1/2 | 1’’ 1/2
Key:
V - Electrical supply
G - Gas supply
R - System return
M - System delivery
SC - Condensate drain (Ø13mm min. internal)

## Slide 9
Delivery flow pipe G 1 ½’’
Return flow pipe G 1 ½’’
Safety valve connection
Condansate drain
Antifreeze kit
Lower Cover
Victrix 35-55-80 Pro V2
Victrix 100-120-150-180 Pro V2
Gas Pipe
G 3/4’’ (35-55-80)
G 1’’ (100-120-150)
Dimensions and connections

## Slide 10: Main components; 55-60-68-80 models
Flue connection D.80-125 with condensate drain discharge
Air vent valve
Thermalfuse
IsoPower condesing module
B&P Spark generator
Detection electrode
Air intake
Venturi Polidoro
EBM Fan
Drain condensate
WILO pump
Sit 848 gas valve
Pressure Transducer
Safety valve 4 bar

## Slide 11: Main components 100-120-150 models
Air vent valve
Thermalfuse
Duo Power condensing module
Spark generator:
B&P (for 100-120 models )
Brahma (for 150 boiler)
Ignition electrode
EBM Fan
WILO pump
Gas valve
Drain condensate
Pressure Transducer
Safety valve 5,4 bar
Flue connection D.110-160 with condensate drain discharge
Detection electrode
Air intake
Venturi Polidoro
Gas collector

## Slide 12: Sealed chamber; 55-60-68-80 models
Unlike the previous range, the new models have a sealed chamber made with the sides of the casing and a front sealed chamber cover.
side sealing strips
Upper closing plate S.C
Frame
Sealed Chamber front panel
Hinges

## Slide 13: Sealed chamber; 100-120-150-180 models
side sealing strips
Upper closing plate S.C
Frame
Sealed Chamber front panel
Hinges

## Slide 14
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 15
Hydraulic circuit
Victrix PRO 100- 120 - 150
Victrix PRO 35 – 55 - 80

## Slide 16
VICTRIX PRO 60-68-80 V2 Condensing module
V-PRO 60-68-80 V2
IsoPower 7+2 module
V-PRO 55 V2
IsoPower 5+2 module
V-PRO 35 V2
IsoThermic 4+1
V-PRO 100
Condensing module 8+4
Compared to previous versions, there is no plant flow sensor on condensing modules with composite casing, because the feedback-pump signal is used to intercept the locked rotor.
In this way the burner is stopped immediately.

## Slide 17
Condensing module 12+6
VICTRIX PRO V2 Condensing module
Condensing module 10+5
Condensing module 15+8
VICTRIX PRO 150
VICTRIX PRO 180
VICTRIX PRO 100

## Slide 18
Victrix Pro 35-55-60-68 and 80 V2 different in circulators type and some connection pipes.
New CAMPINI 5.5 bar transducer, for all boilers versions
Pipe diameter 18 mm ( for 35 ) and 22 mm ( from 55 up to 80 )
Flow and return NTC probes
Safety valve 4 bar
CAMPINI pressure transducer
Drain connection pipe
WILO pump
PARA 15/8- 75 W for 35
PARA 15/8- 87 W for 55
Flow and return pipes
Overheating Safety Thermostat 105°C
WILO pump
PARA MAXO 25/10-130
Victrix 35-55 Pro V2
Victrix 60-68-80 Pro V2
Hydraulic circuit
Safety valve 4 bar
Drain connection pipe
Drain Funnel
Drain funnel

## Slide 19
Hydraulic circuit - Circulator
Victrix Pro V2 60-68-80-100-120 EU
LED STATUS
LED off: circulator not powered
fixed Green LED: circulator powered or running
flashing Red LED (temporary error): pump is making attempts to unblock; overload; pump driven by external flow; overtemperature;
overvoltage; undervoltage
fixed Red LED (permanent error): pump blocked (unblock the rotor mechanically - de-energise for approx 30 sec. in order to reset the pump's internal error); faulty motor
Red / Green flashing LED (signalling): dry running; overload; overtemperature; undervoltage
Victrix Pro V2 35-55 EU
LED
LED
During DHW mode, the circulator pump always runs at full speed.

## Slide 20
Saftey valve 5,4 bar
WILO pump
PARA MAXO 25-10-130
Return flange G 1 ½'' as on circulator
WILO pump
STRATOS PARA T12 25/12
Victrix 100-120 Pro V2
Victrix 150-180 Pro V2
Tubes with a diameter of 35 mm
New WILO pump:
  Wilo PARA MAXO 25/10-130-PWM-F21 ( same for 100-120 )
  Wilo STRATOS PARA T12 25/12-180-PWM-6 ( for 150 )
Hydraulic circuit
Overheating Safety Thermostat 105°
Delivery flow and return pipe d.22
Overheating Safety Thermostat 105°

## Slide 21
Pump flow rate / head
VICTRIX PRO 55 V2
VICTRIX PRO 80 V2

## Slide 22
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 23
Condensing module IsoThermic 4+1
Flue probe with thermal cutoff
Gas manifold same of
Victrix Pro 35-55
Polidoro burner cod. 1.040670
Ignition electrode Victrix Pro
New detection electrode Robertshaw
Fan adapter
Fan EBM VGR100
VICTRIX PRO 35 V2 combustion

## Slide 24
VICTRIX PRO 55 V2 combustion
Iso Power 5+2 module
Flue probe with thermal cut-off
Polidoro burner
Ignition electrode
Victrix Pro
New detection electrode
Fan-manifold adapter
Fan EBM VGR100
Gas manifold Victrix Pro 55
ISOPOWER condensing module 5+2
Gas valve SIT 848 230V
Mixer (Venturi group) placed before the fan (it works in depression, lower friction loss)

## Slide 25
VICTRIX PRO 60-68-80 V2 combustion
IsoPower 7+2 module
Flue probe with thermal cut off
Polidoro burner
Gas manifold Victrix Pro 55
Ignition electrode
Victrix Pro
New detection electrode
New gas manifold cover
with increased height
Fan-manifold adapter
Fan EBM VGR108

## Slide 26
Condensing module 8+4
VICTRIX PRO 100 V2 combustion circuit
Air vent valve
Duo Power 8+4 module
Flue probe with thermal cutoff
Gas manifold for 100-120 models
Ignition electrode
Detection electrode
Fan EBM NRG137
180 W
Module-flange connection

## Slide 27
VICTRIX PRO V2 combustion circuit
Sermeta Duo Power 12+6 module
Flue probe with thermal cutoff
Gas manifold Sermeta for 150
Ignition electrode
Detection electrode
Fan EBM NRG137 300 W
with enlarged inlet
Module-flange connection
Duo Power 10+5 module
Gas manifold Sermeta for 100-120

## Slide 28
Pre-mix system
Gas nozzle
Mixer with double chamber Venturi
The Mixer has a Venturi with modular sections. The non-return valves (clapet), placed inside, partialize the section by the air movement induced by the fan.
The Mixer is positioned before the fan so it works in depression.
It guarantees lower friction loss and higher stability in power output supply.
It allows to obtain an high modulation range (1:10), because the Venturi section changes according with the air/gas flow rate.
Linear functioning even at low power (low fan rpm)
It increases the system efficiency (reducing on/off cycles)

## Slide 29
V_Pro 35 V2
Venturi-Fan adapter
V_Pro 55 V2
V_Pro 60-68-80 V2
Venturi D.26 - Polidoro
Venturi D.30 - Polidoro
Venturi D. 34 - Polidoro
Gas nozzle
Combustion component
Gas nozzle
SIT 848 gas valve is used for all boilers

## Slide 30
Gas nozzle
Sit 822 Gas valve for both boilers version
Victrix Pro 120 V2
Victrix Pro 100 V2
Venturi D.38 Polidoro
Venturi D.34 Polidoro
Combustion component
Venturi-Fan adapter
Leak sprays and liquids clog the pressure feedback hole of the gas valve, damaging it irreparably.
During installation and maintenance, do not use spray or liquids in the upper area of the gas valve.

## Slide 31
Combustion component
Victrix Pro 180 V2
Venturi Resideo
Gas nozzle
Victrix Pro 150 V2
Rambler VK4405 V
Resideo gas valve
Gas nozzle
Leak sprays and liquids clog the pressure feedback hole of the gas valve, damaging it irreparably.
During installation and maintenance, do not use spray or liquids in the upper area of the gas valve.

## Slide 32
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 33: User interface

## Slide 34: User interface
New electronics, including the display board:
Dot matrix display (black LCD with backlight);
Rubber keypad with 12 buttons (with ABS plastic surface);
On-Off knob to cut off the power supply to the single boiler;
Manometer 0-6 bar (There is a pressure transducer to view the system pressure in the Info menu and on communication BUS);
Screw type terminal blocks for the electrical connections on boards placed in the special connection compartment.
2 zones can be managed directly from the boiler electronic (1 zone can be mixed) + DHW tank

## Slide 35: Electronics and user interface
Opening with rotation of the control panel back cover to access the display board, pressure gauge, main switch and control board; compared to today, the control panel is divided into 2 parts, to rationalize access to the electronic parts
Opening with rotation on hinges of the whole control panel.
Opening of the terminals block cover to access the electrical connection boards.

## Slide 36: Electronics and user interface connections
Opening with rotation on hinges of the control panel back cover to access the display board, pressure gauge, main switch and main board
“Low voltage” connection board (thermoregulation device inlets, probes and BUS communication) ( code 1.045932 )
“High voltage” connection board (such as pumps and mixing valves) ( code 1.045933 )

## Slide 37
Rear cover
Connection compartment cover
HIGH tension
clamps
LOW tension clamps
Manometer cover
Pressure
gauge
Display PCB
Keypad
Braker circuit
Front bezel
Sliding cover
Ahestetic frame
Knob
Display cover
Electronics and user interface
Main PCB
CLIP-IN
optional

## Slide 38
Main board (Maxsys III ): ( code 1.045523 )
There is a greater number of relays than the previous electronic board, so that 2 system zones (one mixed) can be managed directly with the boiler electronics;
There are 5 relays 230 Vac that can be used for the outputs / loads and they are multifunctional (the function is assigned via parameter in the menu)
Electronics and user interface

## Slide 39
Buffer capacitor for the internal clock
2 free contact multifunctional relays on the display board
Display board: ( code 1.045527 )
There is a clock and a calendar for programming the heating and DHW time slots;
Black dot Matrix LCD;
There is the clock and date for programming the heating and sanitary time slots (ECO, COMFORT, OFF)
Additional 2 relays are present on the display board that can be used for the loads, also multifunctional (free contact);
The function is assigned via parameter in the menu;.
Electronics and user interface
Keypad

## Slide 40
MAIN SCREEN
MAIN SCREEN ON SLAVE BOILER when the «EASY CASCADE» is connected)
Electronics and user interface
Graphic INTERFACE and menus

## Slide 41
Electronics and user interface: settings
  Example of a submenu
  Central Heating settings
  User menu
  Service menu (password protected)
  User menu
  Central Heating
  DHW
  Holiday
  Settings
  Diagnostic
  Maintenance

## Slide 42
Electronics and user interface: settings
With this electronic board, which has a large number of relays, it is possible to manage 2 heating circuits (2 direct zones, or one direct + one mixed) + DHW tank.
This makes it possible to satisfy most installations, without having to add the cascade manager.
GENERAL SETTINGS
Possibility of parallel operation of DHW and Heating ( for low inertia systems such as fan coils, to simultaneously serve the system and DHW, "inhibiting" DHW priority);
Possibility of programming the CH and DHW time bands (ECO, COMFORT, OFF mode, Holiday, etc, etc…);
previously models there was no time band for either heating or DHW, external thermoregulation was required;
Manual test of multifunction relays that have been programmed;
Maintenance menu with the possibility of entering the Service phone number and the day/month/year of scheduled maintenance;
Air vent function ( standard enabled )
Main probe kits remain confirmed (external probe, storage tank probe, system delivery probe).

## Slide 43
With this electronic board, which has a large number of relays, it is possible to manage 2 heating circuits (2 direct zones, or one direct + one mixed) + DHW tank.
This makes it possible to satisfy most installations, without having to add the cascade manager.
HEATING ZONES
Setting of differentiated 2 temperature sets, possible by setting 2 differentiated temperature curves;
2 free contacts thermostats or standard Open Therm;
Continuous pump function for heating;
DHW OPERATIONS
Management of the DHW operation with 3-way valve (230 Vac) or with external pump;
DHW cylinder can be controlled by NTC sensor or by free contact ( DHW thermostat );
Possible simultaneous DHW and heating functioning;
Anti Legionella (with NTC probe, only)
“EASY CASCADE": with the new boiler electronics you can manage up to 15 Victrix Pro V2 boilers. The limit of 5 boilers remain with IMG FLUES and HYDRAULIC KITS.
Note: The “EASY CASCADE" of the Victrix Pro V2 is not compatible with previous versions (V-Pro V1) due to V2 versions use a Modbus connection.
Electronics and user interface: settings
Notes: Altri termostati OT ? Per il riscaldamento non ci sono problemi, sarebbe da verificare l’eventuale sanitario, se compreso nel termostato.
6 tipologie di richieste riscaldamento (Termostato con curva climatica, Termostato senza curva climatica, solo curva climatica  richiesta sempre presente, Set di temperatura costante  richiesta sempre presente, 0-10 V che agisce su % di potenza, 0-10 V che agisce sul set di temperatura)
Solo curva climatica  richiesta sempre presente, Set di temperatura costante  richiesta sempre presente.
Se voglio usare poi il contatto TA c’è un parametro con cui impostare una riduzione sulla temperatura di mandata o sulla curva climatica.

## Slide 44
  MODBUS (used for BMS and simple cascade)
  OPENTHERM
    2 standard Open-Therm inputs are available, one for each zone;
    Note: If an Open-Therm device is installed as a zone thermostat, DHW regulation can only be controlled if it is connected to the terminals of the first zone (if the device has DHW regulation).
      The Honeywell T3M Thermostat tested in laboratory;
      The 2 OT inputs can be used for 2 clean contact thermostats;
      The IMG-BUS protocol (CAR V2) is not compatible.
  BUS EBV
    New EBV cascade and zones regulator
    Compatible with current EBV cascade and zones regulator (code 3.015244)
    Compatible with current remote control for single boiler (single installation); code 3.020358
    The Clip-In VICTRIX PRO V2 is optional (same one of former VICTRIX PRO)
    Note: When the device code 3.020358 - 3.015244 are used, its mandatory to install the CLIP_IN
  0-10 V inlet is available (same of VICTRIX PRO)
Electronics and user interface: comunication and protocols

## Slide 45
Electronics and user interface: BMS
Remove jumper X40
The Modbus parameters can be found at "Technician menu / SYSTEM SETTINGS / Modbus parameters".
The parameter "CH Request type" must be set as “R.T. setpoint" (default value).
It is possible to connect the following sensors to the device and read them via BUS:
System flow sensor (B1-2)
External probe (B4)
DHW probe (B2)
DHW Thermostat/Contact
Key:
1 - Cable type: twisted pair (20 / 22 AWG)
2 - BMS (MODBUS master)
The DHW can be managed locally (appropriately configure the 3-way valve via the parameters in the "Relay settings" menu.
BMS: a pull-up resistance and a pull-down resistance must be present on the bus.
In the diagram, it is assumed that the two resistances are already present in the external device (for this reason, TR+ should not be connected with T+ and TR- with T-).
The termination resistance (120 ohms) is required on both sides of the BUS.

## Slide 46
2 DIRECT ZONES + DHW 3 –WAY VALVE
Example of hydraulic scheme

## Slide 47
1 DIRECTZONE+ 1 MIXED ZONE + DHW PUMP
Example of hydraulic scheme

## Slide 48
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 49
Electrical wires
High voltage connections
Probe and BUS connections
Display board
MAIN board

## Slide 50
iXTool connections
Probe and BUS connections
Electrical wires
A 37 board:
High voltage connections
The boiler has two boards:
Main P.C.B. (A2)
Display board (A37).
There are 3 fuses on the MIAN board:
A2: 5x20 T 3.15 A H 250V (F1, F2, F4).
On the connection board
A 37 : is type 5x20 6.3 A F 250V (F5).
MIAN board
Display board

## Slide 51: Electrical connections: high voltage connections
  Low voltage connections: Input and BUS communication
* The Master boiler is the one connected to the internal Modbus Master, while the Slave boilers are connected via their Modbus Slave input;
To the Master generator come the probes and activates the loads (pumps and mixing valves ), and "coordinates" all the boilers in cascade.
S1 - S2 | Delivery flow probe
H - R | DHW probe or Thermostat
S3 - S4 | Low temperature zone delivery probe. (mixed zone)
G – J | External probe
OT1 - OT2 | ON/OFF R.T.1 input or Open Therm input
OT3 - OT4 | ON/OFF R.T.2 input or Open Therm input
Y – Z | 0-10 V Analogic Input
R3 - R4 | External RESET button, anomalie in corso
TR- TRD T- T+ TR+ GND | Mod Bus Slave (BMS and EASY Cascade )*
D- D+ TR- TRD T- T+ TR+ GND | Mod Bus Master ( for EASY Cascade )*
M - O | BUS EBV ( for Cascade Regulator /manager )

## Slide 52: Electrical connections: loads on relays of boards
The functionality of all relays is configurable by parameter from User Interface, to make the system more flexible. The multi-function relays are accessible from the terminal block of the electrical connections board.
Power supply that gives voltage to relays
N°5 Relays 230 Vac
N°2 Relays with potential free-contacts
Multi-function relays (230 V) | Current | NOTES
K70-A1 / K70-A2 / K70-A3 / K70-A4 / K70-A5 | < 0.1 A | From factory settings, K70 relays do not perform any functions.
K70-A6 / K70-A7 | Free contact < 0.1 A | Insert an optional external relay to drive each load.
Maximum loads on relays of boards: for pumps and mixing valves and other devices are as follow…

## Slide 53
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Optional
VICTRIX PRO V2

## Slide 54
Insert the combustion analyser in the dedicated holes placed on the top of the boiler;
Enable the «Chimney sweep» by the Technical Menu/Manual Test path, allows the technician to check combustion parameters;
Pressing the 'OK' button activates the function and displays the power percentage that can be changed with the '+' and '-' buttons.
After around 5 minutes, compare the CO2 value with the one reported in the instruction booklet;
In case of need, set the correct value with screw n°3;
Gas | CO2 Min. heat output
G20 (natural gas) | 8,90
G31 (propane) | 10,00
Example with VICTRIX PRO 100
CO2 regulation (min. power)

## Slide 55
CO2 regulation (max power)
Enable the «Chimney sweep» by the Technical Menu/Manual Test path, allows the technician to check combustion parameters;
Pressing the 'OK' button activates the function and displays the power percentage that can be changed with the '+' and '-' buttons.
After around 5 minutes, compare the CO2 value with the one reported in the instruction booklet;
In case of need, set the correct value with screw n°12
Gas | CO2 Min. heat output
G20 (natural gas) | 9,60
G31 (propane) | 10,60
Example with VICTRIX PRO 100
90%

## Slide 56
CO2 regulation on V_PRO V2 model 150-180
Quando e come va regolato il CO2 al max??
Solo quando regolo il max o anche al min??
Foto del venturi interno ??
Smontare venturi inter???

## Slide 57
Main features
Hydraulic Circuit
Gas and Flue Circuit
User interface
Electronic card and parameter programming
Calibration
Accessories and Options
VICTRIX PRO V2

## Slide 58
IPX5D Victrix Pro 35- 55- 80 V2 cover kit
Cod. 3.033670
IPX5D Victrix Pro 100-120 V2 cover kit
Cod. 3.033671
Accessories and Optional

## Slide 59
IPX5D Victrix Pro 150 V2 cod. 3.033672
IPX5D Victrix Pro Pro 180 V2 cod. 3.033689
Accessories and Optional

## Slide 60
Air intake cap D.80 cod. 3.033759
Installed on V-Pro V2 from 35 to 80.
Is used witht the follow kit
3.015254
3.015255
3.015256
3.024295
3.033715
Accessories and Optional

## Slide 61
3.032715
3.032716
3.032713
3.032714
3.033716
Air intake cap D.100 cod. 3.033760
Installed on V-Pro 100-120-150 V2
Is used witht the follow kit
Accessories and Optional

## Slide 62
Vertical flue kit D.100 cod. 3.032713
For Victrix Pro 100-120-150 V2 models
Stainles Steel vertical flue kit D.100
cod. 3.032714
Accessories and Optional

## Slide 63
Concentric vertical Kit D.80-125
cod. 3.033786
V_Pro 35-55-80 V2
Concentric vertical Kit D.110-160
cod. 3.033790
Victrix Pro 100-120-150 V2
Accessories and Optional

## Slide 64
Clappè kit D.80 Inox
cod. 3.033715
Insatlled in the box
To use on the flue manifold Kit non supplied from Immergas on Victrix Pro 35-55-80 V2
Accessories and Optional

## Slide 65
Clapè kit D.125 Inox
cod. 3.033716
To use on the flue manifold Kit non supplied from Immergas on Victrix Pro 100-120-150 V2
Accessories and Optional

## Slide 66
Antifreeze Kit for Victrix Pro V2
cod. 3.034125
Only one kit for all range boilers.
Accessories and Optional
Condensate passivator kit V_Pro V2 up to 180 kW
cod. 3.033688
Condensate passivator kit V_Pro V2 up to 80 kW
cod. 3.033687

## Slide 67
Cabinet for VICTRIX PRO V2 55-60-68-80-100-120-150.
NOT suitable for VICTRIX PRO 180 V2
New cabinet VICTRIX PRO V2
Previous cabinet
VICTRIX PRO
VICTRIX PRO V2 technical cabinet

## Slide 68
VICTRIX 100-120-150 PRO V2
VICTRIX 55-60-68-80 PRO V2
3.023949
3.023950
3.023951
3.023949
3.023950
3.023952
Single installation

## Slide 69
Single installation with plate heat exchanger
VICTRIX 100-120-150 PRO V2
VICTRIX 55-60-68-80 PRO V2
Kit including connection pipes, air vent, drain cock and connections for filling and expansion tank.
Plate heat exchanger kit for single installation for V-Pro V2 boilers with the possibility of connection on the right or left side.
Sizing of exchanger with ∆T 20 on boiler side and ∆T 15 on system side on 180 kW version.
Sizing of exchanger with ∆T 20 on boiler side and ∆T 15 on system side on 80 kW version.

## Slide 70
Single installation with dirt separator
VICTRIX 55-60-68-80 PRO V2
Left exit
Right exit
VICTRIX 100-120-150 PRO V2
Kit dirt / mud separator for single installations of all Victrix Pro V2 versions with possibility of connection on both right and left side.

## Slide 71
Hydraulic separator
2 different codes for 35-55 and 80-100-120;
Standard provided with filter placed on the system return;
Cylindrical shape, insulated
Hydraulic options
3 Way – valve
Kit positioned on the system delivery;
Storage tank probe included;
230 V electrical supply;
Available from 35 to 120.
Safety kit for single boiler
Thermometer
Thermometer holder
Manual reset safety thermostat
Cock for pressure gauge
Pressure gauge
Manual reset pressure switch
Cut-off gas valve
Expansion vessel connection
Min. pressure switch

## Slide 72
Thermoregulation options
External probe
Modulating remote control for single boiler
On-Off room thermostat

## Slide 73
CLIP-IN VICTRIX PRO V2
(communication interface between boiler board and regulator)
Victrix Pro and Victrix Pro V2 use the same CLIP-IN, but for Victrix Pro V2 it is option.
Cascade and zones regulator kit V-PRO V2 it is composed of the 2 elements:
an interface part
a DIN bar electrical connection part.
Thermoregulation options: New cascade and zones regulator
The previous regulator is replaced by the new version consisting of the user interface with display and keyboard + the terminal block with inputs and outputs, for the 3 zones standard configuration.

## Slide 74
Cascade regulator device

## Slide 75
Clip-in for EBV bus, for Victrix Pro V2 (cod. 3.034122 )
Thermoregulation options
Unlike the previous model, the CLIP-IN board is not fitted as standard on this version.
If it necessary to connected the boiler at the cascade regulator, it is necessary to have the CLI-IN device.

## Slide 76
Cascade kit regulator for Victrix Pro V2
cod. 3.034119 is composed from:
2) heatcon! MMI 200
MMI 200 is a local display to set the EC 1351 Pro
MMI 200 and EC 1351 Pro are connected by flat cable (BUS EbV)
Each EC 1351 Pro can be connected on one MMI 200
Dimension: 144 x 96 x 29 mm
1) heatcon! EC 1351 Pro
EC 1351 Pro is the main control unit
DIN rail mountable
Dimension: 210 x 90 x 61 mm
Thermoregulation options